## Slide 1
University of Ruhuna
Faculty of Engineering
EV Charging Station with
Hybrid Energy Storage System
OpenDSS + Python EMS — System Architecture & Simulation
Final Year Project Presentation | June 2026
Supervisor: Dr. Perera
Notes: Title slide. Introduce yourself and the project.

## Slide 2
System Overview
Integrated renewable energy system for University of Ruhuna Faculty of Engineering campus
Solar PV
1821.6 kWp
15 buildings
BESS
600 kWh / 100 kW
LiFePO4
SuperCap
1.0 kWh / 100 kW
Transient buffer
EV Charging
2 × 22 kW
AC Type 2
CEB Grid
33kV / 415V
1000 kVA TX
OpenDSS Layer
26-bus 415V LV network model
Real cable sizes and lengths from site SLD
17 PV systems at individual building buses
Voltage calculation at all 24 buses per step
Transformer 1000 kVA 33kV/415V Dyn11 modelled
Python EMS Layer
Real measured EV demand profile (82.8 kW peak)
Per-building load profiles (assumed + real logger)
SOC tracking via energy balance equation
5 EMS rules: peak shave, charge, discharge, SC spike
Results: 50 columns including 24 bus voltages
↔
Notes: Two simulation layers work together every 15-min step.

## Slide 3
OpenDSS Network Model — Campus LV Network
Master.dss
Circuit definition, voltage bases, compilation order
Lines.dss
23 line segments, real cable sizes (50–150mm²), real lengths
Loads.dss
21 loads — per-building profiles, real data for 3 buildings
PVSystem.dss
15 PV systems (Gym+HostelD disabled — overvoltage risk)
LoadShapes.dss
14 loadshapes — 3 real (logger) + 11 assumed + solar
Battery.dss
600 kWh / 100 kW LiFePO4, SOC 15-90%, EXTERNAL mode
SuperCap.dss
1.0 kWh / 100 kW, SOC 20-95%, EXTERNAL mode
Monitors.dss
16 monitors at key buses for post-processing
Notes: 8 DSS files define the complete network model.

## Slide 4
Python EMS — 4 Module Architecture
config.py
All system parameters
BESS 600kWh/100kW, SC 1kWh/100kW
PV total 1821.6 kWp
V limits: 0.94-1.06 pu
CO₂ factor: 0.7123 kg/kWh
load_profiles.py
8 building-type profiles (assumed)
LS_ElecDept — real data logger
LS_Workshop_Real — CT corrected
LS_Civil_Real — real data logger
Solar: PVGIS+PySAM Matara 96-step
ems_controller.py
run_step() — called 96 times per day
5 dispatch rules (B1-B4 + SC)
SOC tracking via energy balance
Voltage at all 24 buses per step
50-column CSV output per scenario
run_simulation.py
5 scenarios: clear/cloudy/high/no-EV/no-solar
init_opendss() compiles DSS model
Calls ems_controller step by step
Saves results to 05_Results folder
Notes: 4 Python files work together. ems_controller is the core.

## Slide 5
EMS Dispatch Logic — 5 Rules per 15-min Step
B1
Charge BESS from Solar
If PV available and SOC < 90% → charge battery at up to 100 kW
SOC tracked via energy balance (not OpenDSS API)
B2
Supply EV from Solar + BESS
Real measured profile (9:00–18:45, peak 82.8 kW at 15:00)
Solar first, BESS supplements if solar insufficient
B3
Evening Load Support
17:30–22:30: BESS discharges to supply faculty load
BESS discharges 90%→15% SOC over evening period
B4
Peak Shaving
If net demand > 204 kW (85% of 240 kW limit)
BESS dispatched to cut peak below threshold
SC
SuperCap Spike Response
If |ΔP| > 30 kW between steps → SC discharges
Covers battery ramp gap (τ = 4.14 s filter constant)
Notes: Each 15-min step: Python runs all 5 rules, sends commands to OpenDSS, reads voltages.

## Slide 6
Simulation Results — Clear Day Normal Load
1821.6 kWp
Active PV Capacity
83.8%
Self-sufficiency
10.75 hrs
Grid-free Period
11,261 kg
CO₂ Saved/day
Daily Energy Balance
PV Generation
13,640 kWh
Faculty Load
2,722 kWh
EV Load
350 kWh
Grid Import
499 kWh
BESS Charged
431 kWh
BESS Discharged
440 kWh
Voltage Compliance — Key Buses
GymBus
1.000 pu
✓
(PV disabled)
HostelDBus
1.000 pu
✓
(PV disabled)
HostelCBus
1.057 pu
✓
(cable upgraded 95mm²)
AuditoriumBus
1.073 pu
✗
(still violating)
LibraryBus
1.072 pu
✗
(still violating)
ElecDeptBus
1.018 pu
✓
(short cable, OK)
Notes: Scenario 1 results. Grid-free from 06:15 to 17:00.

## Slide 7
Overvoltage Findings & Mitigation
Root Cause:
Large PV injection on long LV feeders with light local loads → reverse power flow → voltage rise. Formula: ΔV = (P×R + Q×X) / V²
Bus
Max V
PV / Cable
Mitigation
After Fix
GymBus
1.174 pu
171.8 kWp / 709m
Disable PV
1.000 pu ✓
HostelDBus
1.086 pu
111.5 kWp / 576m
Disable PV
1.000 pu ✓
HostelCBus
1.079 pu
135.3 kWp / 377m
Upgrade cable 70→95mm²
1.057 pu ✓
AuditoriumBus
1.073 pu
210.0 kWp / 549m
Reduce PV to 155 kWp OR pf=0.95
pending ⚠
LibraryBus
1.072 pu
125.1 kWp / 869m
Reduce PV to 97 kWp OR pf=0.95
pending ⚠
Voltage limit: 0.94–1.06 pu (CEB Sri Lanka grid code / IEC 60038)
Notes: 3 of 5 violations resolved. 2 remaining need PV size reduction or reactive power control.

## Slide 8
Real Data Logger Integration
Real
Electrical Dept
Real peak:
33.33 kW
Assumed was:
23.69 kW
Avg PF:
0.976
+41% higher than assumed
Real
Mech Workshop
Real peak:
3.51 kW
Assumed was:
0.31 kW
Avg PF:
0.511
CT Phase 1 reversed — corrected
Real
Civil Dept
Real peak:
13.50 kW
Assumed was:
23.69 kW
Avg PF:
0.865
-43% lower than assumed
Assumed
All Other Bldgs
Real peak:
Varies
Assumed was:
As designed
Avg PF:
0.90
Logger data pending
Workflow: Upload Excel → CT problem check → 96-step profile → update 4 files → run simulation
Notes: 3 buildings have real data. Others still use assumed profiles as fallback.

## Slide 9
Objectives vs Simulation Results
1.
Design and simulate EV charging station with HESS on campus LV network
→
26-bus OpenDSS model with real cable data, 5 scenarios simulated, 96-step daily results
2.
Demonstrate reduced operational costs
→
Grid import reduced to 499 kWh/day. 83.8% self-sufficiency → significant cost saving
3.
Lower carbon emissions
→
11,261 kg CO₂ saved per clear day (0.7123 kg/kWh × PV energy, SEA 2022)
4.
Improved energy utilisation efficiency
→
83.8% local supply, BESS round-trip 94.1%, EV charged from solar (349.7 kWh/day)
5.
Voltage compliance across campus network
→
3/5 violation buses resolved. AuditoriumBus+LibraryBus: PV reduction or pf=0.95 proposed
Notes: All 5 objectives addressed. Objectives 4 and 5 partially met — future work proposed.

## Slide 10
Future Work & Conclusion
Future Work
Real data logger profiles for remaining buildings
PV size optimisation using real P_min_load values
Reactive power control (pf=0.95) for Auditorium + Library
MATLAB/Simulink SC transient analysis (ms timestep)
Harmonic power quality study (OpenDSS Harmonics mode)
Economic analysis: NPV, payback period, LCOE
Field validation after system installation
Key Conclusions
System achieves 83.8% self-sufficiency on clear days
Grid-free operation 06:15–17:00 (10.75 hours)
CO₂ saving: 11,261 kg/day (SEA emission factor)
BESS SOC: 23%→90%→15% — EMS logic confirmed working
3 overvoltage buses resolved through engineering measures
Real data logger shows peak loads differ from assumed (up to 41%)
Phase imbalance found at Workshop (65%) and Civil (CT reversal)
AC-coupled HESS architecture validated in OpenDSS
University of Ruhuna FoE — EV Charging HESS Project — June 2026
Notes: Summarise key findings and open the floor for questions.