We use two 22 kW chargers. Battery SOC should always be in 20%-80%.

Peak shaving

We assume that our maximum faculty load demand is 240KW.  If grid supply power greater than 85% of the maximum 240*(85/100) =204KW , then we need a peak shaving. At that time, we gave additional power of more than 204KW by battery, and 204KW supply by grid. As an example, assume the faculty load is 220kw, PV supply 10kw so grid supply 210kw, so we need peak shaving,204 supply by the grid. And 220-10-204=6 kw supply by battery.

Evening support

we consider whether it is evening (17:30-22:30) or not. If it is evening, we give evening support from the solar and battery. Normally, we stop charging at 4:00 pm, but if there is a vehicle still charging at 4:00,  we give a chance to that vehicle to charge after 4:00. Do not give a chance to arriving new vehicles to charge after 4:00. That EV load is also fully handled by the solar and battery . But unfortunately, during Evening support or at the start of evening time, if the battery SOC reduces to 20, immediately stop supplying power from the battery, and we use the grid to supply power to the faculty load. One a the main condition is we are not using grid power to charge EV .if we have ev load and if we had to use grid power to charge ev that should be indicate as a alert or some method in simulation.

Normal power flow

Normally, check whether the EV is connected or not. If EV does not connect, solar PV will priorities to charge the battery. Excess PV energy is used for EV charging. Still remains more Excess PV energy is used to faculty load if there is more excess energy of PV that is supplied to the grid.

At any time, the grid is not used to charge Bess,

Priority list

- Battery charging (use only solar pv power, do not use the grid )

- EV charging (if excess solar generation is available after supplying the battery charge, use that power; if not or not enough to ev charge, use the excess pv + battery power if battery also equal or low than20% that is a problem that time we have to stop ev charging so requird to genarat alert or some thing because One a the main condition is we are not using grid power to charge EV )

- Faculty load (if excess solar generation is available after supplying the battery charge+ EV load, use that power; if not or not enough, use the battery power , )

- Export to grid (if excess solar generation is available after supplying the battery charge+ EV load + faculty load , supply to the grid.)

I